## Calc Sheet
PROJECTNAME | Project Name | Mineral Gap
DATE | Date Dubmitted | 20221212
Customer Info
CUSTCOMPANYNAME | Customer Company Name | TRC Companies, Inc.
CUSTCONTACTNAME | Customer Contact Name | Jayme Garcia, PE
CUSTCONTACTROLE | Customer Contact Role | Sr. Engineering Project Manager
CUSTCONTACTADDRESS1 | Customer Contact Address Line 1 | 3947 Lennane Drive, Suite 130
CUSTCONTACTADDRESS2 | Customer Contact Address Line 2 | Sacramento, CA 95834
CUSTCONTACTEMAIL | Customer Contact Email | Jayme.Garcia@trccompanies.com
CUSTCONTACTPHONE | Customer Contact Phone | Cell: 916-245-8913
PRS Info
PRSCOMPANYNAME | PRS Company Name | Power Relaying Solutions, PLLC (PRS)
PRSCONTACTNAME | PRS Contact Name | Allen Queen
PRSCONTACTROLE | PRS Contact Role | Electrical Engineer
PRSCONTACTADDRESS1 | PRS Contact Address Line 1 | 7035 Smith Corners Blvd. Suite 100
PRSCONTACTADDRESS2 | PRS Contact Address Line 2 | Charlotte, NC 28269
PRSCONTACTEMAIL | PRS Contact Email | Allen.Queen@relayingsolutions.com
PRSCONTACTPHONE | PRS Contact Phone | Cell: 828-226-1067
Relay Info
RELAYTYPE | Relay Type | SEL 351-7
RELAYNAME | Relay Name | Example Relay 1 | Yes | Append Submittal Date?
Site Information
SITERATING_kVA | Site Rated Capacity (kVA) | 3000
Global Settings
FREQ | System Frequency | 60
ROT | System Rotation | ABC
SYSTEMVOLTAGE_LL | System Voltage (L-L, kV) | 12.47
PTR | PTR | 60
CTR | CTR | 120
CTRPRI | CTR Primary (Amps) | 600
CTRSEC | CTR Secondary (5A, 1A) | 5
VNOM | V Nominal (sec, V) | 119.9926
Under-Voltage Elements
V27P1P | Level 1 Pickup (L-N, p.u.) | 105.5935 | 88% | IEEE 1547 UV Setpoint Level 1
V27P1D | Level 1 Delay (cycles) | 120
V27P2P | Level 2 Pickup (L-N, p.u.) | 59.9963 | 50% | IEEE 1547 UV Setpoint Level 2
V27P2D | Level 2 Delay (cycles) | 16
Over-Voltage Elements
V59P1P | Level 1 Pickup (L-N, p.u.) | 131.9919 | 110% | IEEE 1547 OV Setpoint Level 1
V59P1D | Level 1 Delay (cycles) | 120
V59P2P | Level 2 Pickup (L-N, p.u.) | 143.9912 | 120% | IEEE 1547 OV Setpoint Level 2
V59P2D | Level 2 Delay (cycles) | 12
V59N1P | Level 1 Pickup (L-N, p.u.) | 11.9993 | 10% | Used in Open-Phase detection logic.
V59N1D | Level 1 Delay (cycles) | 0
Under-Frequency Elements
F81U1P | Level 1 Pickup (Hz) | 59.5 | 99.17% | IEEE 1547 UF Setpoint Level 1
F81U1D | Level 1 Delay (cycles) | 120
F81U2P | Level 2 Pickup (Hz) | 59 | 98.33% | IEEE 1547 UF Setpoint Level 2
F81U2D | Level 2 Delay (cycles) | 16
Over-Frequency Elements
F81O1P | Level 1 Pickup (Hz) | 60.5 | 100.8% | IEEE 1547 OF Setpoint Level 1
F81O1D | Level 1 Delay (cycles) | 120
F81O2P | Level 2 Pickup (Hz) | 61 | 101.7% | IEEE 1547 OF Setpoint Level 2
F81O2D | Level 2 Delay (cycles) | 16
Phase Inst. Overcurrent
I50P1P | Level 1 Pickup (sec, Amps) | 10
I50P2D | Level 1 Delay (cycles) | 0.5
I50P2P | Level 2 Pickup (sec, Amps) | OFF
I50P2D | Level 2 Delay (cycles) | 0
I50P3P | Level 3 Pickup (sec, Amps) | 1.389 | 120% | Used to block open-phase logic.
I50P3D | Level 3 Delay (cycles) | 0
I50P4P | Level 4 Pickup (sec, Amps) | 0.11575 | 10% | Used for a "load-check" in open-phase logic. This setting may be below the relay minimum setpoint.
I50P4D | Level 4 Delay (cycles) | 0
Ground Inst. Overcurrent
I50G1P | Level 1 Pickup (sec, Amps) | 5.16
I50G1D | Level 1 Delay (cycles) | 0.01
I50D2P | Level 2 Pickup (sec, Amps) | OFF
I50G2D | Level 2 Delay (cycles) | 0
I50G3P | Level 3 Pickup (sec, Amps) | 1.1575 | 100% | Used to block open-phase logic.
I50G3D | Level 3 Delay (cycles) | 0
Phase Time Overcurrent
I51P1P | Level 1 Pickup (sec, Amps) | 1.32
I51P1C | Level 1 Curve | U3
I51P1TD | Level 1 Time Dial | 0.66
I51P1TM | Level 1 Time Minimum (s) | 0
I51P1TA | Level 1 Time Adder (s) | 0
I51P1R | Level 1 Reset Delay (Y, N) | N
I51P2P | Level 2 Pickup (sec, Amps) | 1.32
I51P2C | Level 2 Curve | U3
I51P2TD | Level 2 Time Dial | 0.66
I51P2TM | Level 2 Time Minimum (s) | 0
I51P2TA | Level 2 Time Adder (s) | 0
I51P2R | Level 2 Reset Delay (Y, N) | N
Ground Time Overcurrent
I51G1P | Level 1 Pickup (sec, Amps) | 1.32
I51G1C | Level 1 Curve | U3
I51G1TD | Level 1 Time Dial | 0.66
I51G1TM | Level 1 Time Minimum (s) | 0
I51G1TA | Level 1 Time Adder (s) | 0
I51T1R | Level 1 Reset Delay (Y, N) | N
I51G2P | Level 2 Pickup (sec, Amps) | OFF
I51G2C | Level 2 Curve | U3
I51G2TD | Level 2 Time Dial | 0.66
I51G2TM | Level 2 Time Minimum (s) | 0
I51G2TA | Level 2 Time Adder (s) | 0
I51G2R | Level 2 Reset Delay (Y, N) | N
Power Elements
PPWR1P | Level 1 Per-Phase Pickup | OFF
P3PWR1P | Level 1 3-Phase Pickup | 437.5 | 105% | Set to a percentage of site facility rating.
PPWR1T | Level 1 Power Type | +WATTS
PPWR1D | Level 1 Delay (cycles) | 16000
PPWR2P | Level 2 Per-Phase Pickup | OFF
P3PWR2P | Level 2 3-Phase Pickup | 0
PPWR2T | Level 2 Power Type | +WATTS
PPWR2D | Level 2 Delay (cycles) | 16000

## Validation (hidden)
Supported Relay Types | Yes/No | Fwd/Rev
SEL 351 | Yes | Fwd
SEL 351-6 | No | Rev
SEL 351-7 |  | None
SEL 351A

## Title Sheet
MINERAL GAP
SETTINGS BASIS
SEL 351-7 RELAY
| Customer Name |  | TRC Companies, Inc.
| Project Name |  | Mineral Gap
| Date Submitted |  | 20221212
Customer Contact
Jayme Garcia, PE
Sr. Engineering Project Manager
TRC Companies, Inc.
3947 Lennane Drive, Suite 130
Sacramento, CA 95834
Jayme.Garcia@trccompanies.com
Cell: 916-245-8913
PRS Contact
Allen Queen
Electrical Engineer
Power Relaying Solutions, PLLC (PRS)
7035 Smith Corners Blvd. Suite 100
Charlotte, NC 28269
Allen.Queen@relayingsolutions.com
Cell: 828-226-1067